## Slide 1
Evaluating the Probability of Infection In a UK Hospice Through A CFD Driven Metric and Experimental Validation
Mohammad Elsarraj, Yasser Mahmoudi & Amir Keshmiri
School of Engineering, University of Manchester, M13 9PL, UK

## Slide 2
www.ManchesterCFD.co.uk
Our Expertise

## Slide 3
www.HeliRidgeGraft.com www.theCASP.com www.Nano-Syn.tech
ManchesterCFD Team’s Commercial Activities
www.AffordableHealthTech.com
www.Thermocill.com
www.VerXisWind.com

## Slide 4
Introduction

## Slide 5
Infection Risk in Indoor Spaces
The COVID-19 pandemic exposed the vulnerability of indoor environments to airborne disease transmission.
Airborne transmission remains a critical challenge in enclosed environments like offices, hospitals, and schools.
Smaller aerosol particles (<5 μm) can remain suspended and travel far, unlike larger droplets that settle quickly.
Ventilation plays a crucial role in reducing infection risk and preventing cross-infection
The pandemic has highlighted the importance of robust infection risk (IR) assessment and mitigation strategies.
It exposed major limitations in current infection risk (IR) assessment methods, which often oversimplify transmission mechanisms.

## Slide 6
Ventilation
Purpose of Ventilation:
To remove indoor pollutants and replace stale air with fresh outdoor air in rooms, zones, or entire buildings.
Mixing Ventilation:
Actively mixes fresh air throughout the space to ensure uniform air quality.
Displacement Ventilation:
Gently pushes out contaminated air by introducing fresh air at low levels.
Relies on buoyancy-driven, laminar flow to minimise disruption.
Mixing Ventilation
Displacement Ventilation

## Slide 7
Exhaled Particle Mechanics

## Slide 8
Methodology

## Slide 10
As the governing equations for the mass, momentum, and energy equations, Navier-Stokes is used to model the unsteady incompressible flow field using an Eulerian approach:
The Eulerian Model
where, is the density and is the turbulent heat flux vector, respectively.

## Slide 11
The momentum equation for particles is derived from the balance between inertial forces and external forces applied to the particle:
where, for a spherical particle with a diameter of immersed in continuous air, is the gravitational force exerted on the particle, is the additional exerted forces on the surface of the particle and is the momentum relaxation time scale computed as:
where, is the density of the continuous phase and is the projected area of the particle. The Drag force is modelled through the Schiller-Naumann Correlation, which is a function of the particle Reynolds number:
A small means the particle responds quickly to changes in the fluid velocity (typical of small or light particles).
A large ​ means the particle has inertia, resisting rapid changes and taking more time to align with the fluid motion (common in heavy or large particles).
The Lagrangian Model

## Slide 12
The time-dependent concentrations of quanta (defined as the dose required to cause infection) concentration at each cell in the CFD simulation will be calculated using an equation that considers the computed local particle volume fraction at each cell:
Infection Risk Metric
Virion Concentration at each Cell
Probability of Infection at each Cell
To determine the received dosage (), which is the number of quanta inhaled by exposed occupants at each computational cell, the inhalation rate and exposure time are essential information. Integrating the above Equation (quanta concentration) across time yields the received number of quanta at each cell ():
where, is the simulation time. This resembles the exposed occupants at any point in the room who have already ingested a given quantity of viral load within a specific time period. This is what generates the spatial-temporal infection map. Finally, the probability of infection at each cell () can be computed through the application of the Wells-Riley model:

## Slide 13
We employ a POI metric which accounts for the particle number, exposure duration, and clinical data. This metric computes the emission and distribution of infectious airborne particles carrying viral concentrations (quanta) within a room.
Probability of Infection (POI)
Volume fraction of particles to air
The initial hydrated volume of particles
Viral load 2.35 ×109 [quanta/mL]
Inhalation rate [0.6 m3/h]

## Slide 14
Case Study Description

## Slide 15
The Green
Main Entrance
The Case Study

## Slide 16
View A
View B
3
2
2
2
1
1
1
4
Geometry
View B

## Slide 17
Mesh

## Slide 18
Mesh

## Slide 19
Initial CFD Results

## Slide 20
Energy Modelling

## Slide 21
 | Energy Modelling (IESVE) | CFD (Star-CCM+)
Spatial resolution | Buildings at zone level | Detailed single room/zone analysis
Temporal resolution | Annual at 1-15 min time-step | Several minutes/hours at seconds time step
Conservation equations | Quasi-steady energy and mass conservation | Navier-Stokes equations
Computing cost | Low | High
CFD vs Energy Modelling

## Slide 22
Validation

## Slide 23
Validation Framework

## Slide 24
Experimental Setup
A
B
C
D
S1
S2
S3
S4
S5
S6
View A
View B
View D
View C
West Facing Wall
East Facing Wall
North Facing Wall
South Facing Wall

## Slide 28
Occupancy | Time of Day
Minimum | 11:45
Q1 | 12:16
Q2 | 12:39
Q3 | 13:00
Maximum | 13:20
Validation Cases

## Slide 29
Peak Occupancy @ 13:20
32 occupants

## Slide 30
 | E1 | E2 | E3 | E4 | Intake 1 | Intake 2 | Internal Door 1 | Internal Door 2
Ventilation Rate (kg/s) | 0.1031 | -0.1174 | -0.1065 | -0.0176 | -0.0469 | 0 | 0 | 0
Validation Boundary Conditions
Validation Boundary Conditions

## Slide 33
Infection Risk Assessment

## Slide 34
Challenge: Natural ventilation causes high variability (hour-to-hour, day-to-day) in airflow → difficult to capture with full-year CFD.
Approach:
  Full-year dynamic energy simulation (IES VE → 8,760 hrs of data)
  Statistical analysis of ventilation flow rates across all openings
  Python script identified 13 representative hours (min, max, median, Q1–Q3 across openings)
Benefit:
  Captures full statistical range of natural ventilation behaviour
  Reduces 8,760 hrs → 13 targeted CFD cases
  Ensures coverage of realistic operating conditions while keeping simulations.
Generating Representative Cases

## Slide 35
Representative Cases: Boundary Conditions
Date | Time | Intake 1 | Intake 2 | E1 | E2 | E3 | E4 | ID1 | ID2 | Occupancy | Season
05/07/2023 | 17:30 | -0.04 | 1.01 | -0.33 | -0.5 | 0.89 | -0.05 | -0.51 | 1.39 | 50% | Summer
08/01/2023 | 12:30 | 0 | 0 | 0 | -0.09 | -0.17 | 0.35 | 0 | 0 | 100% | Winter
31/05/2023 | 06:30 | 0.37 | -0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 25% | Summer
17/01/2023 | 15:30 | 0 | 0 | 0.12 | 0.64 | -0.38 | -0.26 | 0 | 0 | 50% | Winter
08/12/2022 | 08:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50% | Winter
24/06/2023 | 07:30 | -0.2 | 0.25 | -0.01 | -0.01 | 0.01 | -0.03 | 0 | 0 | 50% | Summer
16/05/2023 | 16:30 | 0 | 0 | 0.04 | 0.21 | -0.09 | 0.12 | 0 | 0 | 50% | Summer
10/12/2022 | 19:30 | 0 | 0 | 0.11 | -0.07 | -0.05 | -0.02 | 0 | 0 | 100% | Winter
11/07/2023 | 15:30 | -0.07 | -0.36 | 0.5 | 0.31 | -0.42 | -0.16 | 0.5 | -1.25 | 50% | Summer
03/01/2023 | 19:30 | 0 | 0 | -0.09 | 0.23 | -0.04 | -0.03 | 0 | 0 | 100% | Winter
05/02/2023 | 09:30 | 0 | 0 | 0.07 | 0.08 | -0.07 | -0.07 | 0 | 0 | 100% | Winter
31/08/2023 | 18:30 | -0.05 | 0 | -0.08 | 0.02 | 0.13 | 0.05 | 0 | 0 | 50% | Summer
04/07/2023 | 14:30 | 0 | 0 | -0.09 | -0.41 | 1.07 | 0.04 | 0 | 0 | 50% | Summer
13 specific hourly cases across the year whose combined ventilation profiles span the full statistical range across all openings.

## Slide 36
If we approximate the number of infectors as:
where is the population prevalence rate and is the maximum design occupancy of the building application defined by CIBSE/ASHRAE. This is usually 10 m2 of floor area per person.
is taken as 7% [Elsarraj et al 2025].
For this case study, N will be taken as the maximum occupancy level (counting seats) for worst case scenario (Full occupancy taken as 88).
Acceptable limit of Probability of Infection (POI) found as 7.5% [Elsarraj et al 2025].
Number of Infectors

## Slide 37
Case B
Case A
Case D
Case C
Worst Case Infector Positions

## Slide 38
Worst Case Infector Positions

## Slide 39
Case L
Case M
Case K
Worst Case Infector Positions

## Slide 40
Infection Risk vs CO2 Concentration

## Slide 41
Infection Risk vs CO2 Concentration

## Slide 42
If there is a high CO2 Concentration does not mean high infection risk as there can be no infectious particles in that region but there is still an occupant exhaling CO2. e.g Case B.
This is dependent on the infector position and the direction of airflow which both are extremely transient in practice.
Infection Risk vs CO2 Concentration

## Slide 43
Context: Hospices/hospitals house highly vulnerable individuals → airborne infection control is critical.
Problem with CO₂-only control: CO₂ concentration does not reliably represent infection risk.
Solution: Use Probability of Infection (POI) metric, derived from CFD simulations, to quantify airborne risk (0–100%).
Validation approach: Coupled CFD + energy model calibrated with real field data (CO₂, temperature, wall conditions, airflow).
Representative use cases: 13 scenarios from year-long ventilation data captured realistic airflow patterns and worst-case infector positions.
Findings: POI-based thresholds recommend earlier window opening:
  Begin at 500 ppm
  Fully open at 600 ppm
  Linear control within ±50 ppm
Impact: Compared to pre-pandemic 950 ppm threshold, new strategy reduces infection risk while adding only 8% heating demand.
Takeaway: Infection risk (IR) metrics provide a more reliable, representative basis for ventilation control than CO₂ alone, ensuring safety without major energy penalties.
Conclusion

## Slide 44
Tel: +44 (0) 161 529 3514
www.ManchesterCFD.co.uk
info@ManchesterCFD.co.uk